# Auto-Seal Roller Curtain Door (WK Model# WT-R) Specifications

## Part 1 – General

  - Description: Provide roller curtain door(s) factory assembled with frame(s), tracks, wire rope, winch, and all operating components in accordance with contract specifications and approved drawings.

  - Acceptable Manufacturers: Roller curtain door shall be as supplied by Walz & Krenzer, Inc (203-267-5712; sales@wkdoors.com).

  - Standards: Comply with the provisions of the following (as applicable):

- AISC “Specifications for Design, Fabrication, and Erection of Structural Steel for Buildings”.

- The Aluminum Assoc. “Aluminum Design Manual”.

- FEMA Bulletin 3-93, #102 & #114.

  - Submittals:

- Manufacturers Data: Submit installation and maintenance manuals for roller curtain door.

- Shop Drawings: Submit shop drawings approved by licensed Professional Engineer for roller curtain door including dimensional plans, elevations, sections, details for all mountings/connections, and parts list.

- Calculations (optional for critical applications): Submit calculations approved by licensed Professional Engineer verifying the roller curtain door’s ability to withstand the design pressure loading.

- QA Submittals: Submit test reports showing compliance with specified performance characteristics.

  - Qualifications: Manufacturer shall present evidence attesting to at least five years successful experience in the design and manufacture of similar closures.

## Part 2 – Products

- Product Description: Auto-Seal Roller Curtain Door shall be Model WT-R as supplied by Walz & Krenzer, Inc.

- Materials:

- Panel: custom extruded aluminum shape.

- Frame: stainless steel.

- Support Chassis: ASTM A-36 steel.

- Gasket: EPDM foam gasket.

- Finish: extruded aluminum mill finish.

- Design:

- Design Pressure: # (in feet of water). Specify seating (pushing gate closed) or unseating direction (pushing gate open).

- Roller curtain door can be used as an everyday roller curtain door.

- Mounting configurations: on outside face of building, inside the jambs and on the inside face of building.

- Bottom frame is stiffened sheet metal shape designed to be recessed into floor surface to achieve a flush bottom sill.

- Roller curtain door is fully motorized and actuates by pressing a button on a wired control station. Remote control actuation is also available.

- Gate will automatically close if a float switch detects water (can be disabled if desired).

- Infrared sensor provided to detect movement through door opening during lowering of door. If triggered, door will fully open and automatically close after a pre-determined period.

- UPS is provided for operation during power loss.

- Power requirements: 120 VAC, 30 A circuit.

- Frame(s) shall have mounting holes for expansion.

- Quality Assurance:

- Perform shop operational test to open/close barrier.

- Perform shop hose leakage test.

# Part 3 – Execution

- Fabrication:

- The finished product shall be rigid, neat in appearance, and free from all defects, warps, and buckles.  All exposed joints and corners shall be well rounded.

- The panel and frame shall be flat within 1/8” in any 6’ length.

- All butt welds in frame to be full penetration welds.

- Installation:

- Install roller curtain door in accordance with manufacturer’s instructions and approved shop drawings.

- After installation, perform field operational test per manufacturer’s instructions to verify seal.

- Finish paint (if applicable) after installation.

- Warranty: Roller curtain door shall operate satisfactorily and be free of defects in material and workmanship for a period of not less than one year from the date of delivery.