# Watertight Door with Compression Gasket (WK Model# WT-FD-I) Specifications

## Part 1 – General

  - Description: Provide watertight door(s) factory assembled with frame and all operating components in accordance with contract specifications and approved drawings.

  - Acceptable Manufacturers: Watertight door shall be as manufactured by Walz & Krenzer, Inc (203-267-5712; sales@wkdoors.com).

  - Standards: Comply with the provisions of the following (as applicable):

- AISC “Specifications for Design, Fabrication, and Erection of Structural Steel for Buildings”.

- The Aluminum Assoc. “Aluminum Design Manual”.

- AWS Structural Welding Code D1, D1.2, D1.3, D1.6.

- ASME Structural Welding Code Section IX.

- FEMA Bulletin 3-93, #102 & #114.

- ASTM A36, D2000.

- American Iron and Steel Institute (AISI) CL 304, 316, 316L.

  - Submittals:

- Manufacturers Data: Submit installation and maintenance manuals for watertight door.

- Shop Drawings: Submit shop drawings approved by licensed Professional Engineer for watertight door including dimensional plans, elevations, sections, details for all mountings/connections, and parts list.

- Calculations (optional for critical applications): Submit calculations approved by licensed Professional Engineer verifying the watertight door’s ability to withstand the design pressure loading.

- QA Submittals: Submit test reports showing compliance with specified performance characteristics.

  - Qualifications: Manufacturer shall present evidence attesting to at least five years successful experience in the design and manufacture of similar closures.

## Part 2 – Products

- Product Description: Watertight door shall be Model WT- FD-I as manufactured by Walz & Krenzer, Inc.

- Materials:

- Panel: A-36 steel (aluminum and stainless steel available).

- Frame: A-36 steel (aluminum and stainless steel available).

- Gasket: ASTM D2000 GR DE neoprene gasket, 25 duro with fully molded corners.

- Dogs/Drop bolts: stainless steel/bronze dogs or drop bolts. Utilize drop bolts for reduced maintenance and lower cost where operation is from outside only.

- Finish: Aluminum panel painted with INSL-X CheckRust acrylic paint. Frame blast clean per SSPC-SP7 and primed with inorganic zinc primer. Other finishes, including powder coating and anodizing available.

- Grab Handle and Panel Stops: 6061-T6 aluminum

- Hinges: to include bronze oil-impregnated thrust bearing and stainless steel hinge pins.

- Design:

- Design Pressure: # (in feet of water). Specify seating (pushing door closed) or unseating direction (pushing door open).

- Side frames are angles for mounting on the exterior face of the wall surface.

- Bottom frame is a flatbar with raised machined knife-edge. Standard bottom sill is raised 1-1/2” from floor surface.

- Roller assembly is provided on gates wider than 6’.

- Frame(s) shall have mounting holes for expansion anchors (options include masonry subframe with welded anchors for embedment in concrete).

- Frame knife-edge shall be rounded and smooth to maximize sealing.

- Removable ramp (optional) is placed over the raised bottom sill for vehicular traffic or to prevent tripping hazard.

- Door size and design pressure direction shall determine the quantity and type of dog. Dogs are designed to adjust gasket compression in the field.

- Quality Assurance:

- Perform shop operational test.

- Perform shop chalk test.

- Liquid Penetrant Test (for critical applications): Welds in the “potential” leak path shall be liquid penetrant inspected in accordance with Appendix VIII of Section VIII of ASME Code Div. 1.

- Hydrostatic Test (optional for critical application): Provide hydrostatic test data certifying that the closure furnished, or a closure of similar design, has been satisfactorily tested to verify that it will withstand the designed hydrostatic pressure with no visible leakage.

Part 3 – Execution

- Fabrication:

- The finished product shall be rigid, neat in appearance, and free from all defects, warps, and buckles.  All exposed joints and corners shall be well rounded.

- The panel and frame shall be flat within 1/8” in any 6’ length.

- All butt welds in frame to be full penetration welds.

- Installation:

- Install watertight door in accordance with manufacturer’s              instructions and approved shop drawings.

- After installation, perform field operational and chalk test per manufacturer’s instructions to verify seal.

- Finish paint (if applicable) after installation.

- Warranty: Watertight door shall operate satisfactorily and be free of defects in material and workmanship for a period of not less than one year from the date of delivery