# Removable Inflatable Gasket Flood Barrier (WK Model# FP-I) Specifications

## Part 1 – General

  - Description: Provide flood barrier(s) factory assembled with frame(s) and all operating components in accordance with contract specifications and approved drawings.

  - Acceptable Manufacturers: Flood barrier shall be as manufactured by Walz & Krenzer, Inc (203-267-5712; sales@wkdoors.com).

  - Standards: Comply with the provisions of the following (as applicable):

- AISC “Specifications for Design, Fabrication, and Erection of Structural Steel for Buildings”.

- The Aluminum Assoc. “Aluminum Design Manual”.

- AWS Structural Welding Code D1, D1.2, D1.3, D1.6.

- ASME Structural Welding Code Section IX.

- FEMA Bulletin 3-93, #102 & #114.

  - Submittals:

- Manufacturers Data: Submit installation and maintenance manuals for flood barrier.

- Shop Drawings: Submit shop drawings approved by licensed Professional Engineer for flood barrier including dimensional plans, elevations, sections, details for all mountings/connections, and parts list.

- Calculations (optional for critical applications): Submit calculations approved by licensed Professional Engineer verifying the flood barrier’s ability to withstand the design pressure loading.

- QA Submittals: Submit test/inspection reports showing compliance with specified performance characteristics.

  - Qualifications: Manufacturer shall present evidence attesting to at least five years successful experience in the design and manufacture of similar closures.

## Part 2 – Products

- Product Description: Removable flood barrier shall be Model FP-I as manufactured by Walz & Krenzer, Inc.

- Materials:

- Panel: 5051-H32 aluminum plate with 6061-T6 aluminum stiffeners (mild steel and stainless steel options are available).

- Frame: ASTM A-36 steel (options include aluminum and 304 or 316 stainless steel).

- Latches: stainless steel sliding latch bolts.

- Gasket: Dual EPDM inflatable gasket supplied with standard automotive style valve stem and 0-60 psi pressure gauge. Fabric reinforced inflatable gasket used for his pressure applications or large size barriers.

- Finish: aluminum panel painted with INSL-X CheckRust acrylic paint. Mild steel frame to be blast to near white metal per SSPC-SP-7 and primed with one coat of inorganic zinc primer. Finish coat with epoxy paint is available.

- Grab Handle and Panel Stops: 6061-T6 aluminum (mild steel and stainless options are available).

- Storage brackets: ASTM A-36 steel.

- Design:

- Design Pressure: # (in feet of water). Specify seating (pushing gate closed) or unseating direction (pushing gate open).

- Side frames are available as angles for mounting on the exterior face of the wall surface, or as flatbars for mounting inside door jambs.

- Bottom frame is a ½” flatbar, which can be recessed ½” into floor surface to achieve a flush bottom sill.

- Corners of flood barrier to have a minimum 7” radius at frame.

- Optional air sources: compressed air tank, hand and foot pump.

- Frame(s) shall have mounting holes for expansion anchors (options include masonry subframe with welded anchors for embedment in concrete).

- Multiple panel flood barriers available with a center mullion.

- Sealing surfaces shall be finished to 63 micro inches to maximize sealing, uninterrupted by steps greater than 0.015”, free of cracks, with finish lay parallel to seal.

- Two (2) storage brackets per panel included.

- Additional requirements such as hydrodynamic loads, impact loads and breaking wave loads shall be added as required by the specific application.

- Quality Assurance:

- Perform shop operational test.

- Perform shop chalk test.

- Air leakage test: inflate gaskets and confirm no loss of pressure over ½ hour time period.

- Liquid Penetrant Test (for critical applications): Welds in the “potential” leak path shall be liquid penetrant inspected in accordance with Appendix VIII of Section VIII of ASME Code Div. 1.

# Part 3 – Execution

- Fabrication:

- The finished product shall be rigid, neat in appearance, and free from all defects, warps, and buckles.  All exposed joints and corners shall be well rounded.

- The panel and frame shall be flat within 1/8” in any 6’ length.

- All butt welds in frame to be full penetration welds.

- Installation:

- Install flood barrier in accordance with manufacturer’s instructions and approved shop drawings.

- After installation, perform field operational and chalk test per manufacturer’s instructions to verify seal.

- Finish paint (if applicable) after installation.

- Warranty: Flood barrier shall operate satisfactorily and be free of defects in material and workmanship for a period of not less than one year from the date of delivery.